## Input_Output_Data
Input |  |  |  |  | Output
Current Conditions |  | Alternate Scenario |  |  | Current Conditions |  | Alternate Scenario
Activated Sludge Input Data |  | Activated Sludge Input Data |  | SRT (day) | Approximate Operating Conditions |  | Approximate Operating Conditions
Temperature (°C) | 20 | Temperature (°C) | 20 | 1 | Total average daily flow rate (mgd) | 1 | Total average daily flow rate (mgd) | 1
So (mg/L) | 200 | So (mg/L) | 200 | 2 | Aeration volume in service (mil gal) | 1 | Aeration volume in service (mil gal) | 1
V (mil gal) | 1 | V (mil gal) | 1 | 4 | Influent BOD5 concentration (mg/L) | 200 | Influent BOD5 concentration (mg/L) | 200
Q (mgd) | 1 | Q (mgd) | 1 | 6 | Influent BOD5 mass loading (lb/day) | 1668 | Influent BOD5 mass loading (lb/day) | 1668
Inert VSS (mg/L) | 40 | Inert VSS (mg/L) | 40 | 8 | Sec ww Oxid N load (lb/day) | 291.9 | Sec ww Oxid N load (lb/day) | 291.9
Oxidizable N (mg/L) | 35 | Oxidizable N (mg/L) | 35 | 10 | Sec ww TSS load (lb/day) | 1668 | Sec ww TSS load (lb/day) | 1668
biomass (VSS/TSS) | 0.85 | biomass (VSS/TSS) | 0.85 | 12 | F/M ratio | 0.08921 | F/M ratio | 0.08921
Influent TSS (mg/L) | 200 | Influent TSS (mg/L) | 200 | 14 | Solids Retention Time (day) | 28 | Solids Retention Time (day) | 28
Inert Inorg TSS (mg/L) | 20 | Inert Inorg TSS (mg/L) | 20 | 16 | MLSS (mg/L) | 2999.8943 | MLSS (mg/L) | 2999.8943
Effluent TSS (mg/L) | 8 | Effluent TSS (mg/L) | 8 | 18 | MLVSS (mg/L) | 2241.9101 | MLVSS (mg/L) | 2241.9101
RAS TSS (mg/L) | 10000 | RAS TSS (mg/L) | 10000 | 20 | TSS Sludge Production (lb/day) | 826.8199 | TSS Sludge Production (lb/day) | 826.8199
MLSS (mg/L) | 3000 | MLSS (mg/L) | 3000 | 22 | TSS in activated sludge effluent (lb/day) | 66.72 | TSS in activated sludge effluent (lb/day) | 66.72
fd | 0.1 | fd | 0.1 | 24 | Total Oxygen Requirements (lb/day) | 3121.4485 | Total Oxygen Requirements (lb/day) | 3121.4485
Y | 0.6 | Y | 0.6 | 26 | Total Oxygen Req'd W/Denit. (lb/day) | 2686.9241 | Total Oxygen Req'd W/Denit. (lb/day) | 2686.9241
Ks (mg/L) | 60 | Ks (mg/L) | 60 | 28 | Total oxygen supplied (lb/day) | 3394.1588 | Total oxygen supplied (lb/day) | 3184.7307
kd at 20°C (1/day) | 0.1 | kd at 20°C (1/day) | 0.1 | 30 | Mixing intensity in the reactor (hp/mil gal) | 150 | Mixing intensity in the reactor (hp/mil gal) | 85
k at 20°C (1/day) | 8 | k at 20°C (1/day) | 8 | 32 | RAS flow rate (mgd) | 0.42855 | RAS flow rate (mgd) | 0.42855
|  |  |  | 34 | RAS recycle percentage (%) | 42.855 | RAS recycle percentage (%) | 42.855
Aerator Performance Data |  | Aerator Performance Data |  | 36 | WAS flow rate (mgd) | 0.0099139 | WAS flow rate (mgd) | 0.0099139
|  |  |  | 38 | RAS TSS concentration (mg/L) | 10000 | RAS TSS concentration (mg/L) | 10000
Operating DO concentration (mg/L) | 4.5 | Operating DO concentration (mg/L) | 2 | 40 | Total sludge production (lb/day) | 893.5399 | Total sludge production (lb/day) | 893.5399
alpha | 0.84 | alpha | 0.84 | 42 | Reactor Detention Time (hr) | 24 | Reactor Detention Time (hr) | 24
beta | 0.92 | beta | 0.92 | 44 | VOLR (lb BOD/(thou cu ft-day)) | 12.4766 | VOLR (lb BOD/(thou cu ft-day)) | 12.4766
SOTR, lb O2 / hp-hr | 2.7 | SOTR, lb O2 / hp-hr | 2.7 | 46 | Effluent CBOD5 (mg/L) | 3.9944 | Effluent CBOD5 (mg/L) | 3.9944
Temperature (°C) | 20 | Temperature (°C) | 20 | 48 | Effluent TSS (mg/L) | 8 | Effluent TSS (mg/L) | 8
Aeration (hp) being operated | 150 | Aeration (hp) being operated | 100 | 50 | Effluent Ammonia-N (mg/L) | 0.37528 | Effluent Ammonia-N (mg/L) | 0.37528
Elevation (ft) | 200 | Elevation (ft) | 200 | 52 | Effluent NO3-N (mg/L) | 26.0246 | Effluent NO3-N (mg/L) | 26.0246
Aerators operating time (hr/day) | 24 | Aerators operating time (hr/day) | 24 | 54 | Effluent NO3-N W/denit (mg/L) | 7.8074 | Effluent NO3-N W/denit (mg/L) | 7.8074
Type of aerators (1, 2, or 3) | 1 | Type of aerators (1, 2, or 3) | 1 | 56
Speed of aerators (%) | 100 | Speed of aerators (%) | 85 | 58 | Actual Aerator Performance |  | Actual Aerator Performance
Energy cost unit ($/kWh) | 0.09 | Energy cost unit ($/kWh) | 0.09 | 60
|  |  |  | 62 | Field OTR ( lb O2 / hp-hr) | 0.94282 | Field OTR ( lb O2 / hp-hr) | 1.5611
|  |  |  | 64 | Aerator energy use (kWh/month) | 70200 | Aerator energy use (kWh/month) | 39780
|  |  |  | 66 | Energy cost ($/month) | 6318 | Energy cost ($/month) | 3580.2
|  |  |  | 68 |  |  | Cost savings vs. current conditions ($/month) | 2737.8
70
Note on C4: Temperature of the mixed liquor.
Note on C5: BOD5 concentration in influent to activated sludge process.
Note on C6: Volume of activated sludge reactor(s).
Note on C7: Influent wastewater flow rate.
Note on C8: Non-biodegradable VSS in influent to activated sludge process. Typical values are 20 to 80 mg/L.
Note on C9: Potential oxidizable nitrogen (≈ TKN) in influent to activated sludge process.
Note on C10: Typical biomass VSS/TSS ratio.
Note on C11: Total Suspended Solids concentration in influent to activated sludge process.
Note on C12: Inorganic (fixed) Suspended Solids in influent to activated sludge process. Typical values are 10 to 50 mg/L.
Note on C13: Total Suspended Solids concentration in effluent from activated sludge process.
Note on C14: Total Suspended Solids concentration in the return activated sludge (RAS).
Note on C15: Total Suspended Solids concentration in the mixed liquor.
Note on C16: Fraction of biomass that remains as cell debris. Typical values are 0.1 to 0.15.
Note on C17: Biomass yield constant. Typical values are 0.4 to 0.8.
Note on C18: Half-saturation constant. Typical values are 25 to 100 mg/L.
Note on C19: Microbial decay coefficient. Typical values are 0.06 to 0.15 1/day.
Note on C20: Maximum specific substrate utilization rate. Typical values are 3 to 16 1/day.
Note on C24: Dissolved oxygen concentration to be maintained in the mixed liquor
Note on C25: Oxygen transfer coefficient in wastewater ÷ oxygen transfer coefficient in tap water.
Note on C26: Saturation DO concentration in wastewater ÷ saturation DO concentration in tap water
Note on C27: Standard oxygen transfer rate in tap water at 20°C, zero DO, & sea level Ultra-fine bubble diffusers 3.7 Fine bubble diffusers 3.1 Medium bubble diffusers 2.4 Coarse bubble diffusers 1.9 Surface slow speed 3.1 Surface slow speed w/ draft tube 2.8 Surface high speed 2.7 Surface downdraft turbine 2.6 Submerged turbine w/ sparger 2.6 Submerged impeller 2.6 Surface brush & blade 2.7 Surface Orbal disc 2.4 Static tube system 2.3 Jet 2.9 Aspirator 2.1
Note on C28: Temperature of the mixed liquor.
Note on C29: Total aeration capacity (horsepower).
Note on C30: The altitude of the region above sea level.
Note on C31: Hours per day aeration units are operating.
Note on C32: 1- Mechanical Aerators (50% to 100% speed) 2- Positive Displacement Blowers (≥ 50% speed) 3- Centrifugal Blowers (typically can only run at 90% speed or greater)
Note on C33: Aerator speed as % of maximum speed. Typical values are 50 to 100%.
Note on C34: Overall cost of electricity in $/kWh; it includes base kWh cost, demand charges, and all fees.
Note on F4: Temperature of the mixed liquor.
Note on F5: BOD5 concentration in influent to activated sludge process.
Note on F6: Volume of activated sludge reactor(s).
Note on F7: Influent wastewater flow rate.
Note on F8: Non-biodegradable VSS in influent to activated sludge process. Typical values are 20 to 80 mg/L.
Note on F9: Potential oxidizable nitrogen (≈ TKN) in influent to activated sludge process.
Note on F10: Typical biomass VSS/TSS ratio.
Note on F11: Total Suspended Solids concentration in influent to activated sludge process.
Note on F12: Inorganic (fixed) Suspended Solids in influent to activated sludge process. Typical values are 10 to 50 mg/L.
Note on F13: Total Suspended Solids concentration in effluent from activated sludge process.
Note on F14: Total Suspended Solids concentration in the return activated sludge (RAS).
Note on F15: Total Suspended Solids concentration in the mixed liquor.
Note on F16: Fraction of biomass that remains as cell debris. Typical values are 0.1 to 0.15.
Note on F17: Biomass yield constant. Typical values are 0.4 to 0.8.
Note on F18: Half-saturation constant. Typical values are 25 to 100 mg/L.
Note on F19: Microbial decay coefficient. Typical values are 0.06 to 0.15 1/day.
Note on F20: Maximum specific substrate utilization rate. Typical values are 3 to 16 1/day.
Note on F24: Dissolved oxygen concentration to be maintained in the mixed liquor
Note on F25: Oxygen transfer coefficient in wastewater ÷ oxygen transfer coefficient in tap water.
Note on F26: Saturation DO concentration in wastewater ÷ saturation DO concentration in tap water
Note on F27: Standard oxygen transfer rate in tap water at 20°C, zero DO, & sea level Ultra-fine bubble diffusers 3.7 Fine bubble diffusers 3.1 Medium bubble diffusers 2.4 Coarse bubble diffusers 1.9 Surface slow speed 3.1 Surface slow speed w/ draft tube 2.8 Surface high speed 2.7 Surface downdraft turbine 2.6 Submerged turbine w/ sparger 2.6 Submerged impeller 2.6 Surface brush & blade 2.7 Surface Orbal disc 2.4 Static tube system 2.3 Jet 2.9 Aspirator 2.1
Note on F28: Temperature of the mixed liquor.
Note on F29: Total aeration capacity (horsepower).
Note on F30: The altitude of the region above sea level.
Note on F31: Hours per day aeration units are operating.
Note on F32: 1- Mechanical Aerators (50% to 100% speed) 2- Positive Displacement Blowers (≥ 50% speed) 3- Centrifugal Blowers (typically can only run at 90% speed or greater)
Note on F33: Aerator speed as % of maximum speed. Typical values are 50 to 100%.
Note on F34: Overall cost of electricity in $/kWh; it includes base kWh cost, demand charges, and all fees.
Bio-Tiger Model
Analysis
Revert to default

## Calculations_Current
SRT | F/M Ratio | Se | Heter Biomass | Cell debris | Inert VSS | MLVSS | MLSS | Biomass Prod VSS | Sludge Prod VSS | T. Solids Prod TSS | Effluent TSS | Intent Waste TSS | Oxygen Reqd | O2 Reqd w/ nit | Eff NH3-N | Eff NO3-N | O2 Reqd w/ den saving | Nit O2 Demand | WAS Flow | N Reduction by Assim. | N Reduction by Assim. | Eff CBOD5 | RAS Flow Rate
day |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | lb/day | lb/day | lb/day | lb/day | lb/day | lb/day | lb/day | mg/L | mg/L | lb/day | lb/day | mgd | lb/day | mg/L | mg/L | mgd
1 | 1.425 | 17.8378 | 99.3612 | 0.99361 | 40 | 140.3548 | 178.0645 | 836.959 | 1170.559 | 1485.0576 | 66.72 | 1418.3376 | 1090.3669 | 1173.2712 | 20.6617 |  |  | 82.9043 | 0.017006 | 100.4351 | 12.0426 | 22.6914 | 0.018129
2 | 0.72659 | 8.5714 | 191.4286 | 3.8286 | 80 | 275.2571 | 349.7143 | 814.2223 | 1147.8223 | 1458.3086 | 66.72 | 1391.5886 | 1238.5758 | 1424.34 | 18.2381 | 2.4377 | 1383.638 | 185.7642 | 0.016686 | 96.8925 | 11.6178 | 13.2317 | 0.036239
4 | 0.39358 | 4.7191 | 334.7673 | 13.3907 | 160 | 508.1579 | 649.5976 | 725.9093 | 1059.5093 | 1354.411 | 66.72 | 1287.691 | 1412.1728 | 1797.5277 | 14.1453 | 6.7022 | 1685.6225 | 385.3549 | 0.01544 | 84.9314 | 10.1836 | 9.0235 | 0.069473
6 | 0.28225 | 3.5294 | 442.0588 | 26.5235 | 240 | 708.5824 | 911.2734 | 651.3295 | 984.9295 | 1266.67 | 66.72 | 1199.95 | 1532.9592 | 2124.9056 | 9.627 | 11.8001 | 1927.8837 | 591.9464 | 0.014388 | 74.9029 | 8.9812 | 7.5162 | 0.10026
8 | 0.22535 | 2.9508 | 525.4645 | 42.0372 | 320 | 887.5016 | 1147.649 | 591.6205 | 925.2205 | 1196.4241 | 66.72 | 1129.7041 | 1624.9842 | 2424.0357 | 4.8571 | 17.4152 | 2133.2596 | 799.0515 | 0.013546 | 66.8531 | 8.016 | 6.6552 | 0.12964
10 | 0.19022 | 2.6087 | 592.1739 | 59.2174 | 400 | 1051.3913 | 1366.3427 | 543.2603 | 876.8603 | 1139.5298 | 66.72 | 1072.8098 | 1697.9355 | 2620.5297 | 2.2216 | 20.8462 | 2272.4677 | 922.5942 | 0.012863 | 60.3019 | 7.2304 | 6.0629 | 0.15826
12 | 0.16606 | 2.3827 | 646.7476 | 77.6097 | 480 | 1204.3573 | 1572.1851 | 503.4283 | 837.0283 | 1092.6686 | 66.72 | 1025.9486 | 1757.3245 | 2742.5955 | 1.1368 | 22.5295 | 2366.4274 | 985.271 | 0.012302 | 54.8737 | 6.5796 | 5.6162 | 0.18655
14 | 0.14824 | 2.2222 | 692.2222 | 96.9111 | 560 | 1349.1333 | 1768.3922 | 470.098 | 803.698 | 1053.4565 | 66.72 | 986.7365 | 1806.6608 | 2821.403 | 0.86906 | 23.2792 | 2432.7176 | 1014.7421 | 0.011831 | 50.3005 | 6.0312 | 5.2619 | 0.21483
16 | 0.13444 | 2.1024 | 730.6987 | 116.9118 | 640 | 1487.6105 | 1957.1889 | 441.817 | 775.417 | 1020.1847 | 66.72 | 953.4647 | 1848.3185 | 2885.8601 | 0.7065 | 23.8433 | 2487.7568 | 1037.5416 | 0.011432 | 46.3908 | 5.5624 | 4.9728 | 0.24335
18 | 0.12337 | 2.0096 | 763.6774 | 137.4619 | 720 | 1621.1393 | 2140.1639 | 417.5279 | 751.1279 | 991.6093 | 66.72 | 924.8893 | 1883.9707 | 2937.9747 | 0.65656 | 24.2745 | 2532.6715 | 1054.004 | 0.01109 | 43.0054 | 5.1565 | 4.7327 | 0.27229
20 | 0.11424 | 1.9355 | 792.2581 | 158.4516 | 800 | 1750.7097 | 2318.482 | 396.4459 | 730.0459 | 966.807 | 66.72 | 900.087 | 1914.8339 | 2983.5722 | 0.60398 | 24.6198 | 2572.5025 | 1068.7383 | 0.010792 | 40.041 | 4.8011 | 4.5314 | 0.30183
22 | 0.10655 | 1.875 | 817.2656 | 179.7984 | 880 | 1877.0641 | 2493.0165 | 377.9779 | 711.5779 | 945.0799 | 66.72 | 878.3599 | 1941.8151 | 3023.8801 | 0.54924 | 25.0237 | 2606.0673 | 1082.065 | 0.010532 | 37.4198 | 4.4868 | 4.3617 | 0.33209
24 | 0.099962 | 1.8247 | 839.3307 | 201.4394 | 960 | 2000.7701 | 2664.4354 | 361.6676 | 695.2676 | 925.8913 | 66.72 | 859.1713 | 1965.6052 | 3059.8358 | 0.4927 | 25.3408 | 2636.728 | 1094.2306 | 0.010302 | 35.0818 | 4.2064 | 4.2183 | 0.36322
26 | 0.094239 | 1.7822 | 858.9439 | 223.3254 | 1040 | 2122.2693 | 2833.258 | 347.1587 | 680.7587 | 908.822 | 66.72 | 842.102 | 1986.7396 | 3092.1672 | 0.43464 | 25.727 | 2662.6121 | 1105.4275 | 0.010097 | 32.9801 | 3.9544 | 4.0969 | 0.39533
28 | 0.08921 | 1.7458 | 876.4923 | 245.4178 | 1120 | 2241.9101 | 2999.8943 | 334.169 | 667.769 | 893.5399 | 66.72 | 826.8199 | 2005.6403 | 3121.4485 | 0.37528 | 26.0246 | 2686.9241 | 1115.8082 | 0.0099139 | 31.0777 | 3.7263 | 3.9944 | 0.42855
30 | 0.084747 | 1.7143 | 892.2857 | 267.6857 | 1200 | 2359.9714 | 3164.6723 | 322.4721 | 656.0721 | 879.7789 | 66.72 | 813.0589 | 2022.644 | 3148.1387 | 0.31481 | 26.3137 | 2708.7878 | 1125.4947 | 0.0097489 | 29.345 | 3.5186 | 3.9079 | 0.46299
32 | 0.080753 | 1.6867 | 906.5749 | 290.104 | 1280 | 2476.6788 | 3327.8574 | 311.8844 | 645.4844 | 867.3228 | 66.72 | 800.6028 | 2038.0229 | 3171.4654 | 0.28505 | 26.4767 | 2729.3932 | 1133.4425 | 0.0095996 | 27.7577 | 3.3283 | 3.8352 | 0.49877
34 | 0.077154 | 1.6625 | 919.5649 | 312.6521 | 1360 | 2592.217 | 3489.667 | 302.2556 | 635.8556 | 855.9948 | 66.72 | 789.2748 | 2051.9996 | 3192.8634 | 0.25478 | 26.6296 | 2748.2376 | 1140.8638 | 0.0094637 | 26.2962 | 3.153 | 3.7742 | 0.53602
36 | 0.07389 | 1.6409 | 931.4253 | 335.3131 | 1440 | 2706.7384 | 3650.2805 | 293.4611 | 627.0611 | 845.6483 | 66.72 | 778.9283 | 2064.7576 | 3212.5848 | 0.22406 | 26.7738 | 2765.5515 | 1147.8272 | 0.0093397 | 24.9442 | 2.9909 | 3.7233 | 0.57487
38 | 0.070913 | 1.6216 | 942.2973 | 358.073 | 1520 | 2820.3703 | 3809.8474 | 285.3971 | 618.9971 | 836.1612 | 66.72 | 769.4412 | 2076.4497 | 3230.8397 | 0.19296 | 26.9103 | 2781.5265 | 1154.39 | 0.0092259 | 23.688 | 2.8403 | 3.6809 | 0.61547
40 | 0.068184 | 1.6043 | 952.2995 | 380.9198 | 1600 | 2933.2193 | 3968.4932 | 277.9762 | 611.5762 | 827.4308 | 66.72 | 760.7108 | 2087.2043 | 3249.0021 | 0.16167 | 27.0633 | 2797.1347 | 1161.7979 | 0.0091212 | 22.2381 | 2.6664 | 3.6043 | 0.65796
42 | 0.065673 | 1.5886 | 961.5322 | 403.8435 | 1680 | 3045.3757 | 4126.3244 | 271.1246 | 604.7246 | 819.3701 | 66.72 | 752.6501 | 2097.1297 | 3261.2891 | 0.162 | 27.109 | 2808.659 | 1164.1594 | 0.0090246 | 21.69 | 2.6007 | 3.5886 | 0.70251
44 | 0.063353 | 1.5743 | 970.081 | 426.8356 | 1760 | 3156.9166 | 4283.4313 | 264.7792 | 598.3792 | 811.9049 | 66.72 | 745.1849 | 2106.3185 | 3272.6649 | 0.1623 | 27.1513 | 2819.3285 | 1166.3464 | 0.0089351 | 21.1823 | 2.5398 | 3.5743 | 0.7493
46 | 0.061201 | 1.5613 | 978.0191 | 449.8888 | 1840 | 3267.9079 | 4439.8917 | 258.8859 | 592.4859 | 804.9717 | 66.72 | 738.2517 | 2114.8497 | 3283.2273 | 0.16258 | 27.1906 | 2829.2349 | 1168.3777 | 0.0088519 | 20.7109 | 2.4833 | 3.5613 | 0.79853
48 | 0.0592 | 1.5494 | 985.4098 | 472.9967 | 1920 | 3378.4065 | 4595.7723 | 253.3981 | 586.9981 | 798.5154 | 66.72 | 731.7954 | 2122.7914 | 3293.0605 | 0.16285 | 27.2272 | 2838.4573 | 1170.2691 | 0.0087745 | 20.2718 | 2.4307 | 3.5494 | 0.8504
50 | 0.057332 | 1.5385 | 992.3077 | 496.1538 | 2000 | 3488.4615 | 4751.1312 | 248.2754 | 581.8754 | 792.4887 | 66.72 | 725.7687 | 2130.2028 | 3302.2376 | 0.16309 | 27.2613 | 2847.0641 | 1172.0348 | 0.0087023 | 19.862 | 2.3815 | 3.5385 | 0.90517
52 | 0.055585 | 1.5283 | 998.7606 | 519.3555 | 2080 | 3598.1161 | 4906.0189 | 243.4825 | 577.0825 | 786.85 | 66.72 | 720.13 | 2137.1353 | 3310.822 | 0.16332 | 27.2933 | 2855.115 | 1173.6868 | 0.0086347 | 19.4786 | 2.3356 | 3.5283 | 0.9631
54 | 0.053946 | 1.519 | 1004.8101 | 542.5975 | 2160 | 3707.4076 | 5060.4795 | 238.9885 | 572.5885 | 781.5629 | 66.72 | 714.8429 | 2143.6338 | 3318.8695 | 0.16354 | 27.3232 | 2862.6623 | 1175.2357 | 0.0085713 | 19.1191 | 2.2925 | 3.519 | 1.0245
56 | 0.052406 | 1.5103 | 1010.493 | 565.8761 | 2240 | 3816.3691 | 5214.5519 | 234.7664 | 568.3664 | 776.5958 | 66.72 | 709.8758 | 2149.7379 | 3326.4288 | 0.16374 | 27.3514 | 2869.7516 | 1176.6909 | 0.0085117 | 18.7813 | 2.252 | 3.5103 | 1.0897
58 | 0.050955 | 1.5022 | 1015.8416 | 589.1881 | 2320 | 3925.0298 | 5368.2703 | 230.7922 | 564.3922 | 771.9203 | 66.72 | 705.2003 | 2155.4824 | 3333.5431 | 0.16393 | 27.3779 | 2876.4236 | 1178.0607 | 0.0084556 | 18.4634 | 2.2138 | 3.5022 | 1.159
60 | 0.049586 | 1.4947 | 1020.8846 | 612.5308 | 2400 | 4033.4154 | 5521.6651 | 227.0447 | 560.6447 | 767.5115 | 66.72 | 700.7915 | 2160.8983 | 3340.2506 | 0.16411 | 27.4029 | 2882.7139 | 1179.3523 | 0.0084028 | 18.1636 | 2.1779 | 3.4947 | 1.233
62 | 0.048291 | 1.4876 | 1025.6474 | 635.9014 | 2480 | 4141.5488 | 5674.7632 | 223.5051 | 557.1051 | 763.3472 | 66.72 | 696.6272 | 2166.0128 | 3346.5851 | 0.16428 | 27.4265 | 2888.6545 | 1180.5723 | 0.0083528 | 17.8804 | 2.1439 | 3.4876 | 1.312
64 | 0.047065 | 1.481 | 1030.1527 | 659.2977 | 2560 | 4249.4505 | 5827.5888 | 220.1565 | 553.7565 | 759.4077 | 66.72 | 692.6877 | 2170.8506 | 3352.5771 | 0.16444 | 27.4488 | 2894.2737 | 1181.7265 | 0.0083056 | 17.6125 | 2.1118 | 3.481 | 1.3967
66 | 0.045902 | 1.4748 | 1034.4209 | 682.7178 | 2640 | 4357.1387 | 5980.1632 | 216.9839 | 550.5839 | 755.6752 | 66.72 | 688.9552 | 2175.4335 | 3358.2534 | 0.16459 | 27.4699 | 2899.5969 | 1182.82 | 0.0082609 | 17.3587 | 2.0814 | 3.4748 | 1.4877
68 | 0.044797 | 1.4689 | 1038.4702 | 706.1598 | 2720 | 4464.63 | 6132.5059 | 213.9737 | 547.5737 | 752.1338 | 66.72 | 685.4138 | 2179.781 | 3363.6385 | 0.16474 | 27.49 | 2904.6469 | 1183.8575 | 0.0082184 | 17.1179 | 2.0525 | 3.4689 | 1.5857
70 | 0.043745 | 1.4634 | 1042.3171 | 729.622 | 2800 | 4571.939 | 6284.6341 | 211.1139 | 544.7139 | 748.7693 | 66.72 | 682.0493 | 2183.911 | 3368.7541 | 0.16487 | 27.5091 | 2909.4442 | 1184.8432 | 0.008178 | 16.8891 | 2.0251 | 3.4634 | 1.6915

## Calculations_Alternate
SRT | F/M Ratio | Se | Heter Biomass | Cell debris | Inert VSS | MLVSS | MLSS | Biomass Prod VSS | Sludge Prod VSS | T. Solids Prod TSS | Effluent TSS | Intent Waste TSS | Oxygen Reqd | O2 Reqd w/ nit | Eff NH3-N | Eff NO3-N | O2 Reqd w/ den saving | Nit O2 Demand | WAS Flow | N Reduction by Assim. | N Reduction by Assim. | Eff CBOD5 | RAS Flow Rate
day |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | lb/day | lb/day | lb/day | lb/day | lb/day | lb/day | lb/day | mg/L | mg/L | lb/day | lb/day | mgd | lb/day | mg/L | mg/L | mgd
1 | 1.425 | 17.8378 | 99.3612 | 0.99361 | 40 | 140.3548 | 178.0645 | 836.959 | 1170.559 | 1485.0576 | 66.72 | 1418.3376 | 1090.3669 | 1173.2712 | 20.6617 |  |  | 82.9043 | 0.017006 | 100.4351 | 12.0426 | 22.6914 | 0.018129
2 | 0.72659 | 8.5714 | 191.4286 | 3.8286 | 80 | 275.2571 | 349.7143 | 814.2223 | 1147.8223 | 1458.3086 | 66.72 | 1391.5886 | 1238.5758 | 1424.34 | 18.2381 | 2.4377 | 1383.638 | 185.7642 | 0.016686 | 96.8925 | 11.6178 | 13.2317 | 0.036239
4 | 0.39358 | 4.7191 | 334.7673 | 13.3907 | 160 | 508.1579 | 649.5976 | 725.9093 | 1059.5093 | 1354.411 | 66.72 | 1287.691 | 1412.1728 | 1797.5277 | 14.1453 | 6.7022 | 1685.6225 | 385.3549 | 0.01544 | 84.9314 | 10.1836 | 9.0235 | 0.069473
6 | 0.28225 | 3.5294 | 442.0588 | 26.5235 | 240 | 708.5824 | 911.2734 | 651.3295 | 984.9295 | 1266.67 | 66.72 | 1199.95 | 1532.9592 | 2124.9056 | 9.627 | 11.8001 | 1927.8837 | 591.9464 | 0.014388 | 74.9029 | 8.9812 | 7.5162 | 0.10026
8 | 0.22535 | 2.9508 | 525.4645 | 42.0372 | 320 | 887.5016 | 1147.649 | 591.6205 | 925.2205 | 1196.4241 | 66.72 | 1129.7041 | 1624.9842 | 2424.0357 | 4.8571 | 17.4152 | 2133.2596 | 799.0515 | 0.013546 | 66.8531 | 8.016 | 6.6552 | 0.12964
10 | 0.19022 | 2.6087 | 592.1739 | 59.2174 | 400 | 1051.3913 | 1366.3427 | 543.2603 | 876.8603 | 1139.5298 | 66.72 | 1072.8098 | 1697.9355 | 2620.5297 | 2.2216 | 20.8462 | 2272.4677 | 922.5942 | 0.012863 | 60.3019 | 7.2304 | 6.0629 | 0.15826
12 | 0.16606 | 2.3827 | 646.7476 | 77.6097 | 480 | 1204.3573 | 1572.1851 | 503.4283 | 837.0283 | 1092.6686 | 66.72 | 1025.9486 | 1757.3245 | 2742.5955 | 1.1368 | 22.5295 | 2366.4274 | 985.271 | 0.012302 | 54.8737 | 6.5796 | 5.6162 | 0.18655
14 | 0.14824 | 2.2222 | 692.2222 | 96.9111 | 560 | 1349.1333 | 1768.3922 | 470.098 | 803.698 | 1053.4565 | 66.72 | 986.7365 | 1806.6608 | 2821.403 | 0.86906 | 23.2792 | 2432.7176 | 1014.7421 | 0.011831 | 50.3005 | 6.0312 | 5.2619 | 0.21483
16 | 0.13444 | 2.1024 | 730.6987 | 116.9118 | 640 | 1487.6105 | 1957.1889 | 441.817 | 775.417 | 1020.1847 | 66.72 | 953.4647 | 1848.3185 | 2885.8601 | 0.7065 | 23.8433 | 2487.7568 | 1037.5416 | 0.011432 | 46.3908 | 5.5624 | 4.9728 | 0.24335
18 | 0.12337 | 2.0096 | 763.6774 | 137.4619 | 720 | 1621.1393 | 2140.1639 | 417.5279 | 751.1279 | 991.6093 | 66.72 | 924.8893 | 1883.9707 | 2937.9747 | 0.65656 | 24.2745 | 2532.6715 | 1054.004 | 0.01109 | 43.0054 | 5.1565 | 4.7327 | 0.27229
20 | 0.11424 | 1.9355 | 792.2581 | 158.4516 | 800 | 1750.7097 | 2318.482 | 396.4459 | 730.0459 | 966.807 | 66.72 | 900.087 | 1914.8339 | 2983.5722 | 0.60398 | 24.6198 | 2572.5025 | 1068.7383 | 0.010792 | 40.041 | 4.8011 | 4.5314 | 0.30183
22 | 0.10655 | 1.875 | 817.2656 | 179.7984 | 880 | 1877.0641 | 2493.0165 | 377.9779 | 711.5779 | 945.0799 | 66.72 | 878.3599 | 1941.8151 | 3023.8801 | 0.54924 | 25.0237 | 2606.0673 | 1082.065 | 0.010532 | 37.4198 | 4.4868 | 4.3617 | 0.33209
24 | 0.099962 | 1.8247 | 839.3307 | 201.4394 | 960 | 2000.7701 | 2664.4354 | 361.6676 | 695.2676 | 925.8913 | 66.72 | 859.1713 | 1965.6052 | 3059.8358 | 0.4927 | 25.3408 | 2636.728 | 1094.2306 | 0.010302 | 35.0818 | 4.2064 | 4.2183 | 0.36322
26 | 0.094239 | 1.7822 | 858.9439 | 223.3254 | 1040 | 2122.2693 | 2833.258 | 347.1587 | 680.7587 | 908.822 | 66.72 | 842.102 | 1986.7396 | 3092.1672 | 0.43464 | 25.727 | 2662.6121 | 1105.4275 | 0.010097 | 32.9801 | 3.9544 | 4.0969 | 0.39533
28 | 0.08921 | 1.7458 | 876.4923 | 245.4178 | 1120 | 2241.9101 | 2999.8943 | 334.169 | 667.769 | 893.5399 | 66.72 | 826.8199 | 2005.6403 | 3121.4485 | 0.37528 | 26.0246 | 2686.9241 | 1115.8082 | 0.0099139 | 31.0777 | 3.7263 | 3.9944 | 0.42855
30 | 0.084747 | 1.7143 | 892.2857 | 267.6857 | 1200 | 2359.9714 | 3164.6723 | 322.4721 | 656.0721 | 879.7789 | 66.72 | 813.0589 | 2022.644 | 3148.1387 | 0.31481 | 26.3137 | 2708.7878 | 1125.4947 | 0.0097489 | 29.345 | 3.5186 | 3.9079 | 0.46299
32 | 0.080753 | 1.6867 | 906.5749 | 290.104 | 1280 | 2476.6788 | 3327.8574 | 311.8844 | 645.4844 | 867.3228 | 66.72 | 800.6028 | 2038.0229 | 3171.4654 | 0.28505 | 26.4767 | 2729.3932 | 1133.4425 | 0.0095996 | 27.7577 | 3.3283 | 3.8352 | 0.49877
34 | 0.077154 | 1.6625 | 919.5649 | 312.6521 | 1360 | 2592.217 | 3489.667 | 302.2556 | 635.8556 | 855.9948 | 66.72 | 789.2748 | 2051.9996 | 3192.8634 | 0.25478 | 26.6296 | 2748.2376 | 1140.8638 | 0.0094637 | 26.2962 | 3.153 | 3.7742 | 0.53602
36 | 0.07389 | 1.6409 | 931.4253 | 335.3131 | 1440 | 2706.7384 | 3650.2805 | 293.4611 | 627.0611 | 845.6483 | 66.72 | 778.9283 | 2064.7576 | 3212.5848 | 0.22406 | 26.7738 | 2765.5515 | 1147.8272 | 0.0093397 | 24.9442 | 2.9909 | 3.7233 | 0.57487
38 | 0.070913 | 1.6216 | 942.2973 | 358.073 | 1520 | 2820.3703 | 3809.8474 | 285.3971 | 618.9971 | 836.1612 | 66.72 | 769.4412 | 2076.4497 | 3230.8397 | 0.19296 | 26.9103 | 2781.5265 | 1154.39 | 0.0092259 | 23.688 | 2.8403 | 3.6809 | 0.61547
40 | 0.068184 | 1.6043 | 952.2995 | 380.9198 | 1600 | 2933.2193 | 3968.4932 | 277.9762 | 611.5762 | 827.4308 | 66.72 | 760.7108 | 2087.2043 | 3249.0021 | 0.16167 | 27.0633 | 2797.1347 | 1161.7979 | 0.0091212 | 22.2381 | 2.6664 | 3.6043 | 0.65796
42 | 0.065673 | 1.5886 | 961.5322 | 403.8435 | 1680 | 3045.3757 | 4126.3244 | 271.1246 | 604.7246 | 819.3701 | 66.72 | 752.6501 | 2097.1297 | 3261.2891 | 0.162 | 27.109 | 2808.659 | 1164.1594 | 0.0090246 | 21.69 | 2.6007 | 3.5886 | 0.70251
44 | 0.063353 | 1.5743 | 970.081 | 426.8356 | 1760 | 3156.9166 | 4283.4313 | 264.7792 | 598.3792 | 811.9049 | 66.72 | 745.1849 | 2106.3185 | 3272.6649 | 0.1623 | 27.1513 | 2819.3285 | 1166.3464 | 0.0089351 | 21.1823 | 2.5398 | 3.5743 | 0.7493
46 | 0.061201 | 1.5613 | 978.0191 | 449.8888 | 1840 | 3267.9079 | 4439.8917 | 258.8859 | 592.4859 | 804.9717 | 66.72 | 738.2517 | 2114.8497 | 3283.2273 | 0.16258 | 27.1906 | 2829.2349 | 1168.3777 | 0.0088519 | 20.7109 | 2.4833 | 3.5613 | 0.79853
48 | 0.0592 | 1.5494 | 985.4098 | 472.9967 | 1920 | 3378.4065 | 4595.7723 | 253.3981 | 586.9981 | 798.5154 | 66.72 | 731.7954 | 2122.7914 | 3293.0605 | 0.16285 | 27.2272 | 2838.4573 | 1170.2691 | 0.0087745 | 20.2718 | 2.4307 | 3.5494 | 0.8504
50 | 0.057332 | 1.5385 | 992.3077 | 496.1538 | 2000 | 3488.4615 | 4751.1312 | 248.2754 | 581.8754 | 792.4887 | 66.72 | 725.7687 | 2130.2028 | 3302.2376 | 0.16309 | 27.2613 | 2847.0641 | 1172.0348 | 0.0087023 | 19.862 | 2.3815 | 3.5385 | 0.90517
52 | 0.055585 | 1.5283 | 998.7606 | 519.3555 | 2080 | 3598.1161 | 4906.0189 | 243.4825 | 577.0825 | 786.85 | 66.72 | 720.13 | 2137.1353 | 3310.822 | 0.16332 | 27.2933 | 2855.115 | 1173.6868 | 0.0086347 | 19.4786 | 2.3356 | 3.5283 | 0.9631
54 | 0.053946 | 1.519 | 1004.8101 | 542.5975 | 2160 | 3707.4076 | 5060.4795 | 238.9885 | 572.5885 | 781.5629 | 66.72 | 714.8429 | 2143.6338 | 3318.8695 | 0.16354 | 27.3232 | 2862.6623 | 1175.2357 | 0.0085713 | 19.1191 | 2.2925 | 3.519 | 1.0245
56 | 0.052406 | 1.5103 | 1010.493 | 565.8761 | 2240 | 3816.3691 | 5214.5519 | 234.7664 | 568.3664 | 776.5958 | 66.72 | 709.8758 | 2149.7379 | 3326.4288 | 0.16374 | 27.3514 | 2869.7516 | 1176.6909 | 0.0085117 | 18.7813 | 2.252 | 3.5103 | 1.0897
58 | 0.050955 | 1.5022 | 1015.8416 | 589.1881 | 2320 | 3925.0298 | 5368.2703 | 230.7922 | 564.3922 | 771.9203 | 66.72 | 705.2003 | 2155.4824 | 3333.5431 | 0.16393 | 27.3779 | 2876.4236 | 1178.0607 | 0.0084556 | 18.4634 | 2.2138 | 3.5022 | 1.159
60 | 0.049586 | 1.4947 | 1020.8846 | 612.5308 | 2400 | 4033.4154 | 5521.6651 | 227.0447 | 560.6447 | 767.5115 | 66.72 | 700.7915 | 2160.8983 | 3340.2506 | 0.16411 | 27.4029 | 2882.7139 | 1179.3523 | 0.0084028 | 18.1636 | 2.1779 | 3.4947 | 1.233
62 | 0.048291 | 1.4876 | 1025.6474 | 635.9014 | 2480 | 4141.5488 | 5674.7632 | 223.5051 | 557.1051 | 763.3472 | 66.72 | 696.6272 | 2166.0128 | 3346.5851 | 0.16428 | 27.4265 | 2888.6545 | 1180.5723 | 0.0083528 | 17.8804 | 2.1439 | 3.4876 | 1.312
64 | 0.047065 | 1.481 | 1030.1527 | 659.2977 | 2560 | 4249.4505 | 5827.5888 | 220.1565 | 553.7565 | 759.4077 | 66.72 | 692.6877 | 2170.8506 | 3352.5771 | 0.16444 | 27.4488 | 2894.2737 | 1181.7265 | 0.0083056 | 17.6125 | 2.1118 | 3.481 | 1.3967
66 | 0.045902 | 1.4748 | 1034.4209 | 682.7178 | 2640 | 4357.1387 | 5980.1632 | 216.9839 | 550.5839 | 755.6752 | 66.72 | 688.9552 | 2175.4335 | 3358.2534 | 0.16459 | 27.4699 | 2899.5969 | 1182.82 | 0.0082609 | 17.3587 | 2.0814 | 3.4748 | 1.4877
68 | 0.044797 | 1.4689 | 1038.4702 | 706.1598 | 2720 | 4464.63 | 6132.5059 | 213.9737 | 547.5737 | 752.1338 | 66.72 | 685.4138 | 2179.781 | 3363.6385 | 0.16474 | 27.49 | 2904.6469 | 1183.8575 | 0.0082184 | 17.1179 | 2.0525 | 3.4689 | 1.5857
70 | 0.043745 | 1.4634 | 1042.3171 | 729.622 | 2800 | 4571.939 | 6284.6341 | 211.1139 | 544.7139 | 748.7693 | 66.72 | 682.0493 | 2183.911 | 3368.7541 | 0.16487 | 27.5091 | 2909.4442 | 1184.8432 | 0.008178 | 16.8891 | 2.0251 | 3.4634 | 1.6915

## Charts
Current Conditions
Alternate Scenario

## ©
© | All Rights Reserved.