## Introduction
This Workbook provides an example approach to carbon reduction. There are four tabs: Reference, Carbon Forecast, Example, and Solar.
The reference tabulation provides conversion factors and emission factors used elsewhere in the workbook. An attempt has been made to provide references for much of the information. Other information provided is for information purposes. In particular, informaton from the latest CBECS on energy use in various commercial buildings is provided, along with information on life-cycle carbon emissions from various types of power plants. As Scope 2 emission estimates are highly dependent on the grid factors, an understanding of the reasons for factor variability is helpful.
The calculations and analysis performed within the carbon forecast tab is divided into three separate subsections: Baseline Energy Use and GHG Emissions, Energy Conservation Measures (ECM), and Carbon Forecast. The latter can be used with or without entering the impact of ECM. It is up to the user as to the timing and the basis for the ECM. The current approach presumes a continuation of efforts by power companies to reduce their carbon footprint. This should be reviewed and updated periodically.
The example is provided to help users understand the use of the workbook and provide some ideas on potential areas for carbon reduction. As use of on-site solar may lessen dependence of grid-based electricity, an evaluation approach is provided.
Currently, only Scope 1 & 2 emissions are included. However the approach (benchmark, improving efficiency and making applicable technical and logistical improvements, carbon offset and carbon sequestration) are applicable to Scope 3 emissions as well.
Cells requiring user input are yellow
Cells with reference info or a calculation are gray
Notes and extra info are in blue
Suggested steps in this process include:
Evaluate current carbon emissions
Scope 1: Direct Emission Sources from Company Facilities and Vehicles
Scope 2: Indirect Emissions from Purchased Power
Scope 3: (when Included) Indirect Emissions as a Function of Value Chain
Implement a program of energy conservation measures to minimize GHG emissions
Review current energy use
Identify energy conservation measures
Implement and monitor energy savings
Monitor grid carbon impacts to evaluate status of Scope 2 emissions
Pursue Carbon Offsets and Carbon Sequestration as applicable to achieve corporate goals.
https://www.offsetguide.org/understanding-carbon-offsets/the-role-of-offsets-in-carbon-management-strategies/achieving-carbon-neutrality/
https://www.carbonneutral.com/
https://www.sustain.life/blog/vetted-carbon-offsets
https://www.sustain.life/blog/vetted-carbon-offsets
Questions can be directed to:
Marshall Goers
mgoers@wrpnc.org

## Reference
Notes in blue
MMBTU = million BTU
REFERENCE VALUES FOR USE ON CALCULATIONS
Reference values of conversion factors and emissions coefficients
Conversion Factors
Fuel type to Btu
Electricity | 3412 | Btu/kWh |  |  |  | https://www.rapidtables.com/convert/power/kW_to_BTU.html
Natural Gas | 100000 | Btu/Therm
Fuel Oil #2 | 137999.5584 | Btu/Gallon |  |  |  | https://www.epa.gov/climateleadership/simplified-ghg-emissions-calculator
Propane | 91000 | Btu/Gallon |  |  |  | https://www.epa.gov/system/files/documents/2022-10/Default%20Heat%20Content%20Ratios%20for%20Help%20and%20User%20Guide%20%281%29.pdf | [5 empty] | Downloaded 4/9/2025
Motor Gasoline | 125000 | Btu/Gallon |  |  |  | https://www.epa.gov/system/files/documents/2022-10/Default%20Heat%20Content%20Ratios%20for%20Help%20and%20User%20Guide%20%281%29.pdf
Diesel | 137381 | Btu/Gallon |  |  |  | https://www.epa.gov/system/files/documents/2022-10/Default%20Heat%20Content%20Ratios%20for%20Help%20and%20User%20Guide%20%281%29.pdf
Liquefied Petroleum Gases (LPG) | 92000 | Btu/Gallon |  |  |  | https://www.epa.gov/climateleadership/simplified-ghg-emissions-calculator
Unit Conversions
Water Volumes | 7.481 | gallons/cubic foot
Weight | 2.205 | lb/kg
Weight | 2204.6341 | lb/metric ton
Emission Factors
GHG Emission Factors Hub provides a regularly updated set of default emission factors for organizational greenhouse gas reporting | [5 empty] | https://www.epa.gov/climateleadership/ghg-emission-factors-hub
Stationary Fuels Emission
Fuel Type | lb CO2e/MMBTU | kg CO2e/MMBTU |  | Emission factors from Greenhouse Gas Protocol Emissions Calculation Tool
Natural Gas | 116.9923 | 53.1145
Distillate Fuel Oil No. 2 | 163.4427 | 74.203
Propane | 135.9097 | 61.703
Mobile Fuels |  |  |  | Emission factors from Greenhouse Gas Protocol Emissions Calculation Tool
Fuel Type | Unit | kg CO2e per unit | lb CO2e per unit
Aviation Gasoline | gallon | 8.5368 | 18.8237
Biodiesel (100%) | gallon | 0.012892 | 0.028427
Compressed Natural Gas (CNG) | scf | 7.0838 | 15.6197
Diesel Fuel | gallon | 10.2163 | 22.5269
Ethanol (100%) | gallon | 0.45664 | 1.0069
Jet Fuel | gallon | 9.8295 | 21.674
Liquefied Natural Gas (LNG) | gallon | 7.3835 | 16.2807
Liquefied Petroleum Gases (LPG) | gallon | 5.6997 | 12.5678
Motor Gasoline | gallon | 8.8124 | 19.4313
Residual Fuel Oil | gallon | 11.27 | 24.8503
Electricity
lbs CO2e/kWh
EPA eGrid 2023 SRVC Virgina/Carolina Region |  |  | 0.59342 |  |  | https://www.epa.gov/egrid/summary-data
EPA eGrid 2023 North Carolina |  |  | 0.6264
Table E2. Major fuels consumption intensities by end use, 2018
Major fuels energy intensitya (thousand Btu/square foot in buildings using any major fuel for the end use)
| Total | Space heating | Cooling | Venti- lation | Water heating | Lighting | Cooking | Refrig- eration | Office equip- ment | Com- puting | Other
Principal building activity | kwh/sf
Education | 62.7 | 13.52% | 7.254% | 6.305% | 7.368% | 4.102% | 41.66% | 15.42% | 0.4558% | 0.3418% | 7.824%
Food sales | 232 | 31% | 6.782% | 16.89% | 6.367% | 8.443% | 11.76% | 2.145% | 0.7612% | 4.014% | 17.65%
Food service | 263.3 | 32.38% | 7.139% | 14.8% | 7.553% | 6.156% | 9.726% | 2.069% | 0.6208% | 3.725% | 17.54%
Health care | 144.5 | 26.59% | 5.976% | 23.29% | 2.683% | 15.24% | 6.585% | 2.317% | 1.22% | 4.756% | 17.8%
Inpatient | 193.3 | 18.32% | 7.001% | 14.59% | 19.25% | 8.401% | 16.45% | 4.901% | 0.4667% | 1.4% | 14.47%
Outpatient | 82 | 25.79% | 7.579% | 12.22% | 6.787% | 14.82% | 19% | 8.484% | 0.7919% | 2.262% | 13.24%
Lodging | 85.7 | 25.74% | 9.984% | 18.25% | 1.404% | 18.72% | 15.13% | 5.772% | 0.624% | 1.872% | 16.07%
Mercantile | 88.4 | 25.68% | 6.396% | 9.099% | 9.189% | 12.7% | 17.66% | 9.459% | 0.8108% | 2.432% | 11.62%
Retail (other than mall) | 64.1 | 30.64% | 7.774% | 19.66% | 1.524% | 11.89% | 3.963% | 2.439% | 1.22% | 7.927% | 17.38%
Enclosed and strip malls | 111 | 51.05% | 19.48% | 4.932% | 0.9864% | 6.289% | 6.905% | 3.699% | 0.4932% | 1.233% | 15.17%
Office | 65.6 | 34.99% | 10.66% | 7.068% | 12.4% | 13.33% | 5.214% | 2.317% | 0.6952% | 3.129% | 13.56%
Public assembly | 81.1 | 50.42% | 11.33% | 8.215% | 2.266% | 9.632% | 13.6% | 3.116% | 0.8499% | 0.8499% | 9.632%
Public order and safety | 86.3 | 65.82% | 9.766% | 5.859% | 0% | 15.43% | 3.711% | 2.148% | 0.7812% | 1.562% | 14.45%
Religious worship | 35.3 | 48.92% | 12.07% | 5.263% | 1.548% | 15.79% | 1.548% | 10.22% | 0.3096% | 1.858% | 21.05%
Service | 51.2 | 28.96% | 10.04% | 5.352% | 0.5865% | 9.311% | 4.399% | 1.686% | 0.3666% | 24.34% | 26.54%
Warehouse and storage | 32.3 | 81.11% | 24.88% | 5.53% | 0% | 11.98% | 0% | 2.304% | 0% | 2.765% | 27.19%
Other | 136.4 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Vacant | 21.7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
From CBECS 2018
| Type of Generation | g CO2e/kWh | lb CO2e/kWh | Median lb CO2e/kWh
| Hydropower | 4 | 0.0088106 |  |  | Scope 2 emissions will continue to be dependent on the carbon impacts of various power plant processes. The table to the left provides life-cycle carbon emissions for various power generation processes.
| Wind power | 11 | 0.024229
| Nuclear power | 12 | 0.026432
| Solar power | 41 | 0.090308
| Natural gas | 290-930 | 0.639-2.05 | 1.3436
| Oil | 510-1170 | 1.12-2.58 | 1.8502
| Coal | 740-1689 | 740-1689 | 2.6751
https://www.cowi.com/news-and-press/news/2023/comparing-co2-emissions-from-different-energy-sources/

## Carbon Forecast
Carbon Forecast | [6 empty] | Notes in blue
Input cells
Calculation or fixed text
Baseline Energy Use and GHG Emissions
Value from eGRID for region including North Carolina, Virginia and
https://www.epa.gov/egrid/summary-data
Baseline electric emission coefficient for purchased electricity. |  |  |  | 0.59342 | lbs CO2e/kWh |  |  |  | https://www.residential-carbon-tool.duke-energy.app/
https://residential-carbon-tool.duke-energy.app/residential/main
Summary of Baseline Energy Use and GHG Emissions*
| Type | Source | Usage | Units | Usage million Btu | lb CO2e/yr | Metric Tons per Yr
| Scope 1 | Stationary Sources
|  | Natural Gas |  | therms | 0 | 0 | 0
|  | Fuel Oil |  | gallons | 0 | 0 | 0
|  | Propane |  | gallons | 0 | 0 | 0 | Propane use for heating
Mobile Sources
|  | Gasoline |  | gallons | 0 | 0 | 0
|  | Diesel |  | gallons | 0 | 0 | 0
|  | Propane |  | gallons | 0 | 0 | 0 | Propane use in forklifts and similar vehicles
|  | Refrigerants | [5 empty] | For refrigerants, enter the global warming potential (GWP) in the source column and the projected annual loss. Typical values for a well-maintained system will be below 1%. Common ones are listed below:
|  | GWP |  | lb
| Subtotal Scope 1 |  |  |  | 0 | 0 | 0
| Scope 2 | Electricity |  | kWh | 0 | 0 | 0 |  | Product | GWP |  | Product | GWP
|  | Other |  |  |  |  | 0 |  | R-22 | 1810 |  | R-407C | 1624
| Subtotal Scope 2 |  |  |  | 0 | 0 | 0 |  | R-410a | 1924 |  | R-717 (NH3) | 1 |  | https://www.epa.gov/climate-hfcs-reduction/technology-transitions-gwp-reference-table
| Total |  |  |  | 0 | 0 | 0 |  | R-454b | 466 |  | R-744 (CO2) | 1 |  | https://www.epa.gov/sites/default/files/2016-12/documents/international_transitioning_to_low-gwp_alternatives_in_commercial_refrigeration.pdf
[9 empty] | R-32 | 677 |  | R-404A | 3943 |  | https://www.dcceew.gov.au/environment/protection/ozone/rac/global-warming-potential-values-hfc-refrigerants
| Under Scope 2, "Other" refers to other purchased power. Enter as appropriate. | [7 empty] | R-134a | 1300 |  | R-433B | 3.2 |  | https://ww2.arb.ca.gov/resources/documents/high-gwp-refrigerants
[9 empty] | R-290 (propane) | 3.3 |  | R-600a | 3
Energy Conservation Measures
Projected
|  | Project Description |  |  |  | Impacts |  | % Electricity
Update the grid carbon factor based on the most recent projections. The numbers used assumes a 10% reduction in the grid based carbon factor per year. Duke's carbon plan to be updated in October 2025.
Carbon Emissions Projections
|  |  |  | Projects Impacting Electricity Use and Scope 2 Emissions | [6 empty] | Projects Impacting Scope 1 Emissions
Year Ending | Baseline Emissions | Grid Carbon Factor | Purchased Electricity | [5 empty] | Scope 2 Baseline | Scope 2 Progress |  |  |  | Scope 1 Baseline | Scope 1 Progress | Overall Progress
| lb CO2e/yr | lb CO2e/kwh | kwh/yr | kwh/yr | kwh/yr | kwh/yr | kwh/yr | kwh/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr
2025-12-31 | 0 | 0.59342 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2026-12-31 | 0 | 0.53408 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2028-12-30 | 0 | 0.4326 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2030-12-30 | 0 | 0.35041 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2032-12-29 | 0 | 0.28383 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2034-12-29 | 0 | 0.2299 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2036-12-28 | 0 | 0.18622 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2038-12-28 | 0 | 0.15084 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2040-12-27 | 0 | 0.12218 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2042-12-27 | 0 | 0.098966 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2044-12-26 | 0 | 0.080162 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2046-12-26 | 0 | 0.064931 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2048-12-25 | 0 | 0.052594 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
2050-12-25 | 0 | 0.042601 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0 | 0
Year Ending | Scope 1 Progress | Scope 2 Progress | Overall Progress
2025 | 0 | 0 | 0
2026 | 0 | 0 | 0
2028 | 0 | 0 | 0
2030 | 0 | 0 | 0
2032 | 0 | 0 | 0
2034 | 0 | 0 | 0
2036 | 0 | 0 | 0
2038 | 0 | 0 | 0
2040 | 0 | 0 | 0
2042 | 0 | 0 | 0
2044 | 0 | 0 | 0
2046 | 0 | 0 | 0
2048 | 0 | 0 | 0
2050 | 0 | 0 | 0
Formulas:
Year Ending = +[Year Ending, row above]+365
Year Ending = +[Year Ending, row above]+(365*2)

## Example
Example Carbon Analysis | [6 empty] | Notes in blue
Input cells
Calculation or fixed text
Baseline Energy Use and GHG Emissions
Baseline electric emission coefficient for purchased electricity. |  |  |  | 0.59342 | lbs CO2e/kWh
Summary of Baseline Energy Use and GHG Emissions*
| Type | Source | Usage | Units | Usage million Btu | lb CO2e/yr | Metric Tons per Yr
| Scope 1 | Stationary Sources
|  | Natural Gas | 25000 | therms | 2500 | 292480.7269 | 132.6663
|  | Fuel Oil | 0 | gallons | 0 | 0 | 0
|  | Propane | 0 | gallons | 0 | 0 | 0
Mobile Sources
|  | Gasoline | 1000 | gallons | 125 | 19431.2626 | 8.8138 |  | Assume 2 fleet vehicles driving 15000 miles/year at 30 miles/gallon |  |  |  |  | 500 | gallons per vehicle
|  | Diesel |  | gallons | 0 | 0 | 0
|  | Propane |  | gallons | 0 | 0 | 0
Refrigerants
|  | 1810 | 1 | lb |  | 1810 | 0.821 |  |  |  | For refrigerants, enter the global warming potential (GWP) in the source column and the projected annual loss. Typical values for a well-maintained system will be about 1%. Common ones are listed below:
| Subtotal Scope 1 |  |  |  | 2625 | 313721.9895 | 142.3012
| Scope 2 | Electricity | 2198124.2673 | kWh | 7500 | 1304408.7046 | 591.6667 |  |  |  |  | Product | GWP |  | Product | GWP
|  | Other |  |  |  |  | 0 |  |  |  |  | R-22 | 1810 |  | R-407C | 1624
| Subtotal Scope 2 |  |  |  | 7500 | 1304408.7046 | 591.6667 |  |  |  |  | R-410a | 1924 |  | R-717 (NH3) | 1 |  | https://www.epa.gov/climate-hfcs-reduction/technology-transitions-gwp-reference-table
| Total |  |  |  | 10125 | 1618130.6941 | 733.9679 |  |  |  |  | R-454b | 466 |  | R-744 (CO2) | 1 |  | https://www.epa.gov/sites/default/files/2016-12/documents/international_transitioning_to_low-gwp_alternatives_in_commercial_refrigeration.pdf
[12 empty] | R-32 | 677 |  | R-404A | 3943 |  | https://www.dcceew.gov.au/environment/protection/ozone/rac/global-warming-potential-values-hfc-refrigerants
| Under Scope 2, "Other" refers to other purchased power. Enter as appropriate. | [10 empty] | R-134a | 1300 |  | R-433B | 3.2 |  | https://ww2.arb.ca.gov/resources/documents/high-gwp-refrigerants
[12 empty] | R-600a | 3 |  | R-290 (propane) | 3.3
Energy Conservation Measures
[8 empty] | Projected | LED Lighting |  | HVAC |  | Plant Air |  | Condensate Recovery |  | Improved Motor Mgmt |  | Cooling System
|  | Project Description |  |  |  | Impacts |  | % Electricity | kwh impact | [9 empty] | Start GHG | New GHG
|  | LED Lighting |  |  |  | Scope 2 Emissions |  | 20% | 439624.8535 | Current | 879249.7069 | kwh
|  | HVAC System Tune-Up |  |  |  | Scope 1 & 2 Emissions |  | 40% | 233550.7034 | Future | 10000 | therms
|  | Plant Compressed Air System Optimization |  |  |  | Scope 2 Emissions |  | 15% | 206074.1501 | Reduction | 87924.9707 | kwh reduct'n | 329718.6401 | kwh
|  | Replace Old Boiler/ Implement Condensate Return |  |  |  | Scope 1 Emissions |  | 0% |  |  | 1000 | therms redt'n | 32971.864 | kwh reduct'n | 12500 | therms
|  | Improve Motor Management |  |  |  | Scope 2 Emissions |  | 15% |  |  | 11699.2291 | lb CO2e NG |  |  | 1250 | therms redt'n | 329718.6401 | kwh
|  | Improve systems to minimize refrigerant loss/ Low GWP options |  |  |  | Scope 1 Emissions | [8 empty] | 14624.0363 | lb CO2e NG | 9891.5592 | kwh reduct'n | 1810 | 233
The grid carbon factor used here assumes a 10% reduction in the carbon factor per year. Duke's carbon plan to be updated in October 2025. Check with other electrical providers as appropriate.
Carbon Emissions Projections
|  |  |  | Projects Impacting Electricity Use and Scope 2 Emissions | [6 empty] | Projects Impacting Scope 1 Emissions
Year Ending | Baseline Emissions | Grid Carbon Factor | Purchased Electricity | LED Install | HVAC Improvements | Plant Air Improvements | Motor Mgmt | On-Site Solar | Scope 2 Baseline | Scope 2 Progress | HVAC Improvements | Condensate Return | Low GWP Refrigerant | Scope 1 Baseline | Scope 1 Progress | Overall Progress
| lb CO2e/yr | lb CO2e/kwh | kwh/yr | kwh/yr | kwh/yr | kwh/yr | kwh/yr | kwh/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr | lb CO2e/yr
2025-12-31 | 1618130.6941 | 0.59342 | 2198124.2673 | [5 empty] | 1304408.7046 | 1304408.7046 |  |  |  | 313721.9895 | 313721.9895 | 1618130.6941
2026-12-31 | 1618130.6941 | 0.53408 | 1992050.1172 | 206074.1501 |  |  |  |  | 1304408.7046 | 1063908.3497 |  |  |  | 313721.9895 | 313721.9895 | 1377630.3392
2028-12-30 | 1618130.6941 | 0.4326 | 1904125.1465 |  | 87924.9707 |  |  |  | 1304408.7046 | 823729.2054 | 11699.2291 |  |  | 313721.9895 | 302022.7604 | 1125751.9658
2030-12-30 | 1618130.6941 | 0.35041 | 1871153.2825 |  |  | 32971.864 |  |  | 1304408.7046 | 655667.0519 |  | 14624.0363 |  | 313721.9895 | 287398.7241 | 943065.776
2032-12-29 | 1618130.6941 | 0.28383 | 1861261.7233 |  |  |  | 9891.5592 |  | 1304408.7046 | 528282.7862 |  |  | 1577 | 313721.9895 | 285821.7241 | 814104.5103
2034-12-29 | 1618130.6941 | 0.2299 | 1821261.7233 |  |  |  |  | 40000 | 1304408.7046 | 418712.9496 |  |  |  | 313721.9895 | 285821.7241 | 704534.6737
2036-12-28 | 1618130.6941 | 0.18622 | 1821261.7233 | [5 empty] | 1304408.7046 | 339157.4892 |  |  |  | 313721.9895 | 285821.7241 | 624979.2133
2038-12-28 | 1618130.6941 | 0.15084 | 1821261.7233 | [5 empty] | 1304408.7046 | 274717.5663 |  |  |  | 313721.9895 | 285821.7241 | 560539.2903
2040-12-27 | 1618130.6941 | 0.12218 | 1821261.7233 | [5 empty] | 1304408.7046 | 222521.2287 |  |  |  | 313721.9895 | 285821.7241 | 508342.9527
2042-12-27 | 1618130.6941 | 0.098966 | 1821261.7233 | [5 empty] | 1304408.7046 | 180242.1952 |  |  |  | 313721.9895 | 285821.7241 | 466063.9193
2044-12-26 | 1618130.6941 | 0.080162 | 1821261.7233 | [5 empty] | 1304408.7046 | 145996.1781 |  |  |  | 313721.9895 | 285821.7241 | 431817.9022
2046-12-26 | 1618130.6941 | 0.064931 | 1821261.7233 | [5 empty] | 1304408.7046 | 118256.9043 |  |  |  | 313721.9895 | 285821.7241 | 404078.6284
2048-12-25 | 1618130.6941 | 0.052594 | 1821261.7233 | [5 empty] | 1304408.7046 | 95788.0925 |  |  |  | 313721.9895 | 285821.7241 | 381609.8165
2050-12-25 | 1618130.6941 | 0.042601 | 1821261.7233 | [5 empty] | 1304408.7046 | 77588.3549 |  |  |  | 313721.9895 | 285821.7241 | 363410.079
Year Ending | Scope 1 Progress | Scope 2 Progress | Overall Progress
2025 | 313721.9895 | 1304408.7046 | 1618130.6941
2026 | 313721.9895 | 1063908.3497 | 1377630.3392
2028 | 302022.7604 | 823729.2054 | 1125751.9658
2030 | 287398.7241 | 655667.0519 | 943065.776
2032 | 285821.7241 | 528282.7862 | 814104.5103
2034 | 285821.7241 | 418712.9496 | 704534.6737
2036 | 285821.7241 | 339157.4892 | 624979.2133
2038 | 285821.7241 | 274717.5663 | 560539.2903
2040 | 285821.7241 | 222521.2287 | 508342.9527
2042 | 285821.7241 | 180242.1952 | 466063.9193
2044 | 285821.7241 | 145996.1781 | 431817.9022
2046 | 285821.7241 | 118256.9043 | 404078.6284
2048 | 285821.7241 | 95788.0925 | 381609.8165
2050 | 285821.7241 | 77588.3549 | 363410.079
Formulas:
Year Ending = +[Year Ending, row above]+365
Year Ending = +[Year Ending, row above]+(365*2)

## Solar
Input
Solar PV Application | [11 empty] | Calculation or fixed text
Summary of Recommendations for Assessment Report | [9 empty] | Energy Saving Used in Calculations
Energy Efficiency Recommendations |  |  |  | Cost Savings / yr. |  |  | Investment Cost | Payback Period (years) | mmBtu Saved | Electric KWH | Unit Cost Electric $/kWH
[5 empty] | / yr. |  | Cost | Period | Saved
e.g. Install xxx kW PV Solar Array on Rooftop |  |  |  | 0 |  |  | 0 |  | 0 | 0 | 0
Use this link for solar production estimate:
https://pvwatts.nrel.gov/pvwatts.php
PV Watts Calculator - NREL - National Renewable Energy Laboratory
Step 1: Type in address in the Solar Resource Data Page
Step 2: Click forward to System Date
Use the rooftop estimator to determine the potential size of the system. (uses satellite imagery)
Can be used for ground mounted PV system as well
Review other system settings to leave as default values. Also review Advanced Parameters and adjust as appropriate.
Step 3: Go to Results
Copy kWh annual generation in the Recommendation table above
Suggest Printing Results option to save as PDF for placement in the appendix of reports
Describe system in yellow descrition blow above, e.g., "Install 100 kW PV Solar system on rooftop"
Estimated Rooftop Solar Cost
30% ITC solar tax credit available to both private and public sectors
Installed cost estimate: $1,950 per kW (January 2024 est - Raleigh)
Average PV cost report in 1.66/W or 1,660 per kW for commerical installation
Average PV cost report for residential is $3.08/W or 3,080 per kW for a (smaller) residential installation
Solar Photo Voltaic System Data
Parameter |  |  | Unit |  |  | Remarks
System Size |  |  | kW |  |  | (system type/desc)
Capital Cost |  |  | $ |  |  | includes federal incentives
Incentives |  |  | % |  |  | ITC federal incentive
Annual Production |  |  | kWh/yr
Annual Savings |  |  | $/yr
Solar PV Details
Example Report Body Text A 100 kW roof mounted solar photovoltaic system will produce approximately 150,000 kilowatt-hours of energy annually for savings of $14,250. This constitutes xx% of the facility’s xxx,xxx kWh of electrical energy. The approximate cost of a 100 kW system is $195,000. Recent changes in net metering rules have significantly decreased the amount Duke Energy will pay for solar generation greater than electrical demand of the facility. Therefore it is important not to size the system so large that payback for excess generation is minimal. This issue should be worked out with the system supplier.
A list of Commerial PV Vendors can be found here
https://www.energysage.com/local-data/solar-companies/nc/